TO:		Department Heads

Department Chairmen

###### Hospital Administration

DATE:		September 2022

SUBJECT:	Generator Test: East Tower

The next monthly test is scheduled for Tuesday, September 20, 2022.

- THE EAST TOWER GENERATOR TEST PROCEDURES IS AS FOLLOWS:

1.	The test will be announced over the paging system fifteen minutes prior to the test (5:00 a.m.).

2.	The emergency generators will be started between 5:00 a.m. and 5:05 a.m., and used as the source for the emergency power feed for approximately 60 minutes.

3.	Emergency power will be switched back to the electrical feed between 6:35 a.m. and 6:45 a.m. and the generators turned off.

4.	Completion of the test will be announced over the paging system.

5.	Users of emergency power will notice a series of sequential blinks at the beginning of the East Tower test (one per electrical zone) as each of the 14 emergency power switches are engaged.  At the end of the test, all areas will blink (yellow) as the switches return their respective areas to normal power.

6.	Elevators in the East Tower may stop and start during power transition.

If an unavoidable emergency arises close to the time that the emergency generator test is scheduled and you feel that a brief power interruption would be detrimental to patient care, immediately contact the Maintenance and Operations Center (4-4230).

The test, although intended to simulate an actual power outage, has been modified to keep the disruption to Hospital services at a minimum.  If an actual power outage occurs, the electrical circuits supported by the generator will be without power for 5 to 10 seconds with the exception of those areas which have their own uninterruptible power supplies.  Our recent experience suggests that a real power outage can be expected once a year.  If you have equipment, processes, etc. that cannot cope with a power outage of this duration, your department should consider installing uninterruptible power supplies (UPS's).

If you have any questions or concerns regarding the test or the emergency power system, please feel free to contact Aaron Petty, Facilities Electrical Manager, Physical Plant at extension 47386.

Your continued cooperation in completing the code mandated emergency diesel generator test is greatly appreciated.

Thank you.