ELECTRICAL POWER NOTICE FOR

Downtown Campus Buildings

TO:	All Departments with Space in UH, East Wing, East Tower, CWB, Weiskotten Hall, and Setnor

SUBJECT:	Electric Power Interruptions UH, East Wing, East Tower, CWB, Weiskotten Hall, and Setnor. scheduled for 5:00 am – 6:am am Wednesday, May 14th, 2025

TODAY’S DATE:		May 12th, 2025

WORK PERFORMED ON:	May 14th 2025

Today’s tentative transfer couldn’t be accomplished due to an emergency procedure. In order to return our electric system to normal after National Grid repairs, we will be conducting switching to building feeds listed below between the hours of 5 am and 6am . This will cause power losses from 1 to 10 seconds while we do switching. Emergency power circuits will see a loss similar to generator testing.

***East Wing- Please use OR’s 3,5,and 8 prior to switching and until an all clear is given in the morning.

MRI #2 and Emergency Department CT #1 will also be impacted and should be shut down during switching.

Before any switching is done, we will walk the 5E OR’s, 3N OR’s and 6 West & South Heart & Vascular.

Telemetry monitors may also see a blip and a 1-2 min reboot, but no data will be lost.

This is what you can expect to happen starting at 5:00 a.m.

UH, CWB, East Wing and East Tower; Will experience a loss of some of your normal power circuits for 1 to10 seconds while we conduct switching. Emergency power circuits will see a loss similar to monthly generator testing.

Weiskotten Hall, and Setnor: Some of the normal power circuits will lose power for 1-10 seconds while we conduct switching in the morning. Emergency power will see a loss similar to monthly generator testing. You will see the same impacts in the afternoon when we switch back to normal operations.

Other buildings (Cancer Center,  Gama Knife, Silverman etc.) are not affected.

If you have any questions, please contact Marc Dingle at 315-464-8923