TO: All Departments with Space in the Medical Library, Weiskotten Hall, Weiskotten Hall Addition, New Academic Building, Setnor Academic Building & AC Silverman Hall

DATE: November 2024

SUBJECT:Generator Test: Medical Library, Weiskotten Hall Addition, Weiskotten Hall (including Setnor Academic Building), NAB & Silverman Hall.

The next monthly test is scheduled for **Thursday, November 21, 2024.**

**The test, although intended to simulate an actual power outage, has been modified to keep the disruption to services at a minimum. If an actual power outage occurs, the electrical circuits supported by the generator will be without power for 5 to 10 seconds except for those areas which have their own uninterruptible power supplies. Our recent experience suggests that a real power outage can be expected once a year. If you have equipment, processes, etc. that cannot cope with a power outage of this duration, your department should consider installing uninterruptible power supplies (UPS's).**

**THE WEISKOTTEN HALL TEST PROCEDURES ARE AS FOLLOWS:**

* The emergency generator will be started between 5:00AM and 5:05AM and will be used as the source for emergency power for approximately 30 minutes.
* The emergency power will be switched back to normal between 5:30AM and 5:35AM when the generator turns off.
* Emergency outlets (red) and emergency lights will blink when the test starts and again when it ends.

**THE MEDICAL LIBRARY TEST PROCEDURES ARE AS FOLLOWS:**

* The emergency generator will be started between 6:00AM and 6:05AM and will be used as the source for emergency power for approximately 30 minutes.
* The emergency power will be switched back to normal between 6:30AM and 6:35AM when the generator turns off.
* Emergency outlets (red) and emergency lights will blink when the test starts and again when it ends.

**THE WEISKOTTEN HALL ADDITION TEST PROCEDURES ARE AS FOLLOWS:**

* The emergency generator will be started between 5:00AM and 5:05AM and will be used as the source for emergency power for approximately 30 minutes.
* The emergency power will be switched back to normal between 5:30AM and 5:35AM. when the generator turns off.
* Emergency outlets (red) and emergency lights will blink when the test starts and again when it ends.

**THE NAB and AC SILVERMAN HALL TEST PROCEDURES ARE AS FOLLOWS:**

* The emergency generator will be started between 6:00AM and 6:05AM and will be used as the source for emergency power for approximately 30 minutes.
* The emergency power will be switched back to normal between 6:30AM and 6:35AM when the generator turns off.
* Emergency outlets (red) and emergency lights will blink when the test starts and again when it ends.

If you have any questions or concerns regarding the test or the emergency power system, please feel free to contact Stewart Hatzinger, Facilities Electrical Manager, and Physical Plant at extension 4-8923.

Your continued cooperation in completing the code mandated emergency diesel generator test is greatly appreciated.

Thank you.